## Data collection_example
Table 41: Filled-in example for the data collection sheet - Energy and material balance for biomass gasification plants
1 Data collection and presentation of results |  |  |  | Data collection |  | Data origin (check as applicable) |  |  | Explanation of data origin: e.g. measuring method, calculation path, source of the assumption
|  | Parameters |  | Data | Unit | Calculation | Measure- ment | Assump-tion
Biomass |  | Form |  | Wood shavings |  |  | x |  | Untreated
|  | Origin (within a radius of) |  | 50 | km |  |  | x | Supplier data
|  | Biomass demand at rated operation |  | 109 | kgds/h | x | x |  | Calculation from measured biomass flow (weighing cells) and moisture content
|  | Inferior calorific value |  | 18.7 | MJ/kgds |  | x |  | Laboratory analysis
|  | Moisture content of untreated biomass |  | 30 | wt % |  | x |  | Laboratory analysis
|  | Moisture content of pretreated biomass |  | 10 | wt % |  | x |  | Laboratory analysis
Auxiliary energy |  | Auxilaries with energy content
|  | Auxiliary material 1: | Ignition oil | 9.7 | kWh/L |  |  | x | Bibliographical reference - Source: …
|  | Auxiliary material 2: | RME | 9.5 | kWh/L |  |  | x | Bibliographical reference - Source: …
|  | Auxiliary material 3: | Compressed air (gasifica-tion agent) | - | kWh/L |  |  |  | None
Mass flow of auxiliary material
|  | Auxiliary material 1: | Ignition oil | 2 | L/h |  | x |  | Measurement of the fill cycle of the ignition oil tank
|  | Auxiliary material 2: | RME | 5 | L/h |  | x
|  | Auxiliary material 3: | Compressed air (gasification agent) | 121.5 | L/h |  | x |  | Measurement with orifice flowmeter, continuous
Chem. power of auxiliary material
|  | Auxiliary material 1: | Ignition oil | 19.4 | kW | x |  |  | Calculation from energy content and mass flow of auxiliary materials
|  | Auxiliary material 2: | RME | 47.5 | kW | x
|  | Auxiliary material 3: | Compressed air (gasification agent) | - | kW | x
Power delivered
|  | Therm. power delivered at the total plant (> 20 °C), (auxiliary energy) |  | - | kW |  |  |  | No external thermal auxiliary energy necessary
|  | Electrical power delivered at the total plant (auxiliary energy) |  | 22 | kW |  |  |  | Measurement via own meter
Electrical energy |  | Electrical nominal power |  | 112 | kW |  | x |  | Electricity meter
By-products |  | By-products with energy content
|  | By-product 1: | Wood shavings | 4 | kWh/kg |  |  |  | From biomass processing for pellet manufacturing / analysis of external laboratory
|  | By-product 2: | Coke | 31 | MJ/kg |  |  |  | From gasifier, release as fuel to… / analysis of external laboratory
Mass flow of by-products
|  | By-product 1: | Wood shavings | 10 | kg/h |  |  |  | Measurement upon emptying of receiving container
|  | By-product 2: | Coke | 3.5 | kg/h |  |  |  | Measurement upon emptying of receiving container
Chemical power of by-products
|  | By-product 1: | Wood shavings | 40 | kW | x |  |  | Calculation from energy content and mass flow of by-products
|  | By-product 2: | Coke | 30.1389 | kW | x
Thermal power of by-products (> 20 °C)
|  | By-product 1: | Wood shavings | - | kW |  |  |  | None
|  | By-product 2: | Coke | 10 | kW |  |  |  | Extraction of coke at 250 °C / measurement with thermocouple at receiver
1 Data collection and presentation of results |  |  |  | Data collection |  | Data origin (check as applicable) |  |  | Explanation of data origin: e.g. measuring method, calculation path, source of the assumption
|  | Parameters |  | Data | Unit | Calculation | Measure- ment | Assump-tion
Heat | Thermal Power
| from process 1: |  | Gasification | 56 | kW | x |  |  | Calculation with temperatures measured at heat exchanger
| from process 2: |  | CHP | 227 | kW |  | x |  | Heat meter at CHP
| Drying thermal power |  |  | 28 | kW |  |  |  | Separating out heat downstream of gasifi er for drying of fuel / suitable heat meter
| Nominal heat |  |  | 227 | kW |  |  |  | Addition of all measured heat flows that are available for external utilisation
| Internally used thermal power without drying |  |  | 56 | kW |  |  |  | Preheating of the gasification agent / temperature measurement of gasification agent
| Useful heat |  |  | 170 | kW |  |  |  | Feeding into the heat grid / own heat meter
| Thermal utilisation factor |  |  | 74.8899 | % | x |  |  | Ratio of useful and nominal heat
Residues | Residues and energy content
| Residue 1: |  | … | 24 | MJ/kg |  |  |  | Analysis at external laboratory
| Residue 2: |  | … | 12 | kWh/L |  |  |  | Bibliographical data - Source: …
Mass flow of residues
| Residue 1: |  | … | 1.5 | kg/h |  |  |  | Fill level measurement of receiving container, continuous
| Residue 2: |  | … | 6.5 | L/h |  |  |  | Measurement upon emptying of receiving container
Chemical power of residues
| Residue 1: |  | … | 10 | kW | x |  |  | Calculation from energy content and mass flow of the residues
| Residue 2: |  | … | 78 | kW | x
Thermal power of the residues (> 20 °C), (auxiliary energy)
| Residue 1: |  | … | 14 | kW |  |  |  | Extraction of the fi lter dust at 150 °C / temperature measurement in receiving container
| Residue 2: |  | … | - | kW
Other assumptions | Mass flow of fuel gas after cleaning of crude gas |  |  | 323 | kg/h |  |  |  | Volume flow (orifice plate) and concentration measurement at gasifier outlet
| Gas power of fuel gas |  |  | 388 | kW |  |  |  | Calculation from measured volume flow and composition
| Balanced power loss of the total system |  |  | 83 | kW |  |  |  | Addition of all losses (gasifier, cleaning of crude gas, CHP)
| Non-balanced power loss of the total system |  |  | 0 | kW |  |  |  | Balancing remainder between output / input energy flows
| Total amount of electricity produced |  |  | 186.6667 | MJ/a | x
| Total amount of useful heat produced |  |  | 378.3333 | MJ/a | x
| Annual biomass consumption (untreated) |  |  | 934.2857 | t/a | x
| Annual operating hours |  |  | 6000 | h |  |  |  | Operating hours meter
| Methane slip (CHP) |  |  | - | g/h |  |  |  | Unknown