## Documentation list_example
Table 43: Filled-in example for the documentation list - Balance indicators for biomass gasification plants
2 Indicators of the balancing |  | Data | Units | Calculation | Measurement | Assumption | Explanation of data origin: measuring method, calculation path, source of the assumption
2.1 Biomass pre-treatment (system boundary > Biomass Pre-treatment in Fig 9.)
Fuel power |  | 491.0 | kW | x |  |  | Calculation from measured mass flow and analysis values of fuel
Total rated thermal input |  | 512.0 | kW | x |  |  | Calculation from measured mass flow and analysis values of fuel
Storage and sieve losses (by-product) |  | 40.0 | kW | x |  |  | Calculation from measured mass flow of biofuel (wood shavings) and analysis values of fuel
Drying thermal heat |  | 28.0 | kW |  | x |  | Own heat meter
2.2 Biomass gasifier incl. gas cleaning (system boundary > Biomass Conversion I in Fig 9.)
Gas power |  | 388.0 | kW | x |  |  | Calculation from measured fuel gas volume flow and composition
Power of the by-products (thermal + chemical) |  | 40.0 | kW | x |  |  | Sum of chemical and therm. residue power of the gasifier
Power of residues (thermal + chemical) |  | 102.0 | kW | x |  |  | Sum of power of chemical and thermal by-products of the gasifier
Thermal power (gasification & gas cleaning) |  | 110.0 | kW | x |  |  | Calculated thermal power of gasifi er (product gas volume flow and temperature at gasifier outlet)
Chemical efficiency (cold gas efficiency) |  | 76 | % | x |  |  | Calculation from gas power and total rated thermal input
2.3 CHP or synthesis plant (system boundary > Biomass Conversion II in Fig 9.)
Electrical efficiency of prime mover (gross) |  | 28.8 | % | x |  |  | Calculation from gas & electrical power
Thermal efficiency of prime mover (gross) |  | 58.5 | % | x |  |  | Calculation from gas power & nominal heat of prime mover
Total efficiency of prime mover (gross) |  | 87.2 | % | x |  |  | Calculation from thermal & electrical effi ciency of prime mover
Synthesis efficiency |  | — | % |  |  |  | No synthesis
2.4 Overall plant / system (system boundary > Biomass Pre-treatment in Fig 9.)
Electrical plant efficiency (net) |  | 23.0 | % | x |  |  | Calculation from fuel power and electrical system power
Chemical plant efficiency (net) |  | 14.0 | % | x |  |  | Calculation from fuel power and power of biofuel
Thermal plant efficiency (net) |  | 46.0 | % | x |  |  | Calculation from fuel power and power of usable heat
Total plant efficiency (net) |  | 83.0 | % | x |  |  | Calculation from electrical, chemical / thermal plant efficiency
3 Plausibility check |  | Data | Units | Calculation | Measurement | Assumption | Explanation of data origin: measuring method, calculation path, source of the assumption
3.1 Energy balance (system boundary: ...)
Input | Fuel power | 491.0 | kW | x |  |  | Power of biomass at plant entry relative to the superior calorific value
| Power of auxiliary energy (energy delivered) | 89.0 | kW | x |  |  | Sum of the electrical and thermal auxiliary energy as well as the chemical energy of the individual auxiliaries
| Energy input | 580.0 | kW | x |  |  | Addition of all input energy fl ows - Balance / system boundary (plant entry)
Output | Electrical plant / system power | 112.0 | kW |  | x |  | Corresponds to electrical power of CHP
| Therm. power of plant / system | 227.0 | kW |  | x |  | Corresponds to nominal heat
| Power of by-products (thermal + chemical) | 70.0 | kW | x |  |  | Corresponds to the sum of the chemical power of the by-products
| Power of residues (thermal + chemical) | 88.0 | kW | x |  |  | Corresponds to the sum of the chem. power of the individual residues
| Power loss of gasifier | 15.0 | kW |  |  | x | Thermal loss of gasifier - own assumption - includes thermal power of the by-products (10 kW)
| Power loss of gas cleaning | 19.0 | kW |  |  | x | Thermal loss of crude gas cleaning - own assumption - includes thermal power of the residues (14 kW)
| Power loss of prime mover / synthesis | 49.0 | kW | x |  |  | Calculation via CHP effi ciency (includes heat losses and incomplete combustion)
| Energy output | 580.0 | kW | x |  |  | Addition of all output energy flows - Balance / system boundary (CHP gas outlet)
3.2 Material balance (system boundary ...)
Input | Mass flow of fuel | 156.0 | kg/h |  | x |  | Mass flow of biomass at plant entry
| Mass flow of auxiliaries | 152.0 | kg/h |  | x |  | Sum of mass flows of the individual auxiliaries
| Input mass flow | 308.0 | kg/h | x |  |  | Addition of all input mass flows - balance / system boundary (plant entry)
Output | Mass flow of fuel gas | 287.0 | kg/h | x |  |  | Mass flow at exit of the crude gas cleaning upstream of CHP
| Mass flow of by-products | 14.0 | kg/h |  | x |  | Sum of mass flows of the individual biofuels
| Mass flow of residues | 7.0 | kg/h |  | x |  | Sum of the mass flows of the individual residues
| Mass flow of flue gas (prime mover) | — | kg/h |  |  |  | Mass flow downstream of CHP and flue gas cleaning
| Output mass flow | 308.0 | kg/h | x |  |  | Addition of all output mass flows - Balance / system boundary (CHP gas inlet)