## Data collection_example
Table 45: Hypothetical plant example for the data collection sheet - Energy and material balance for ADs
1 Data collection for balancing |  |  | Data collection |  | Data origin (check as applicable) |  |  | Explanation of data origin: e.g. measuring method, calculation path, source of the assumption
Parameters |  |  | Data | Unit | Calculation | Measurement | Assumption
Biomass 1 | Substrate 1 |  | Cattle manure |  |  |  |  | Operator information
| Origin (within a radius of) |  | 0 | km |  |  | x | Livestock buildings on-site
| Biomass demand at rated operation |  | 21.0 | tFM/d | (x) |  | x | Operator information, alternatively calculation via number of animals
Power of biomass:
| Superior calorific value |  | 14.0 | MJ/kgFM |  |  | x | ECN database
| Dry substance content |  | 10.0 | wt % |  |  | x | KTBL database
| Organic dry solids |  | 8.0 | wt % |  |  | x | Often reference to oDS
| Biogas yield |  | 30.0 | m3/tFM |  |  | x | KTBL database
| Methane content |  | 55.0 | % |  |  | x | KTBL database
Biomass 2 | Substrate 2 |  | Maize silage |  |  |  |  | Operator information
| Origin (within a radius of) |  | 42099 | km |  |  | x | Operator information
| Biomass demand at rated operation |  | 21.0 | tFM/d |  |  | x | Operator information
Power of biomass:
| Superior calorific value |  | 17.0 | MJ/kgFM | x | x | x | ECN database
| Dry substance content |  | 35.0 | wt % |  | x | x | KTBL database
| Organic dry solids |  | 33.3 | wt % |  | x | x | KTBL database
| Biogas yield |  | 261.0 | m3/tFM | x | x | x | KTBL database
| Methane content |  | 52.0 | % | x | x | x | KTBL database
Auxiliary energy | Thermal power delivered of the total plant as annual average |  | – | kW | x |  |  | Generally not received from external
| Electrical power delivered of the total plant as annual average |  | 37.0 | kW | x |  |  | Calculation based on own consumption of electricity of ~8 %, here, coverage by own production
Electrical energy | Electrical nominal power |  | 500.0 | kW | x |  | x | Operator information CHP plant
| Electrical rated power |  | 457.0 | kW | x |  |  | Taking into consideration of the theoretical number of full load hours
By-products | Energy content of by-products
| By-product 1: | … | … | MJ/kg |  |  |  | Calorimetric determination necessary
Mass flow of by-products
| By-product 1: | … | … | kg/h |  |  |  | Operator information, e.g. in plant gate balance
Chemical power of by-products
| By-product 1: | … | … | kW |  |  |  | Calculation based on mass flow and superior calorific value
Heat | Thermal power
| Nominal heat output |  | 577.0 | kW |  |  | x | Gross thermal power of the CHP based on manufacturer's information
| Internally used thermal power |  | 105.0 | kW |  |  | x | Values from literature
| Useful heat output |  | 202.0 | kW |  |  | x | Values from literature
| Thermal utilisation factor |  | 35.0 | % |  |  | x | Based on minimum heat utilisation in accordance with REL 2012
Residues | Residues and energy content
| Residue 1: | Digestate | 16.9 | MJ/kg |  | x |  | Calorimetric determination necessary
| Residue 2: | … | … | MJ/kg |  |  |  | No further residue
Mass flow of residues
| Residue 1: | Digestate | 33.3 | tFM/d | x |  |  | Calculation based on the substrates used
| Residue 2: | … | … | tFM/d | x |  |  | Calculation from balancing (e.g. plant gate balance)
Losses | Methane slip (CHP) |  | 812.0 | g/h | x |  | (x) | Calculation based on the total methane content with 1 % methane slip
| Residual methane potential |  | 5.1 | m³/tFM |  |  | x | Value from literature for multi-stage plants
| Other methane emissions |  | 1,211.0 | g/h |  |  | x | Estimated value for 1.5 % methane slip, to be recorded plantspecific
Other information | Volume flow of biogas |  | 215.0 | m³/h | x |  |  | Calculation based on the theoretical biogas yield
| Methane content |  | 52.0 | % | x |  |  | Calculated via calculation of the ratios of the individual substrates
| Hydrogen sulphide content in crude gas |  | 500 | ppm |  |  | x | Plant-specific measured value
| Gas power of biogas |  | 1,241.0 | kW | x |  |  | Addition of individual yields of the substrates
| Total amount of electricity produced |  | 4,000.0 | MWh/a |  | x |  | Addition of the daily / monthly values from the operations diary
| Total amount of nominal heat produced |  | 4,616.0 | MWh/a |  | x |  | Addition of the daily / monthly values from the operations diary
| Annual biomass consumption (untreated) |  | 15,330.0 | t/a | x |  |  | Sum of the individual substrates based on the operations diaries
| Annual amount of residues |  | 11,948.0 | t/a | x |  |  | Estimated calculation based on the gas yields at a biogas density of 1.25 kg/m3
| Annual amount of by-product |  | … | t/a |  |  |  | Information from balancing (e.g. plant gate balance)
| Annual operating hours CHP |  | 8,500.0 | h/a |  |  | x | To be captured system / plant-specifically
| Annual full load hours CHP |  | 8,000.0 | h/a | x |  |  | Calculatory determination based on the amount of electricity produced and the nominal power (rated power)
| Annual operating hours of the excess gas burner system |  | 50.0 | h/a |  |  | x | To be captured system / plant-specifically