## Documentation list_example
Table 47: Filled-in example for the documentation list - Balance indicators for ADs
2 Indicators of the balancing |  | Data | Unit | Calculation | Measurement | Assumption | Explanation of data origin: measuring method, calculation path, source of the assumption
2.1 Biomass pre-treatment (system boundary > Biomass Pre-treatment in Figure 10.)
Substrate power (related to superior calorific value) |  | 1.718 | kW | x
Storage losses |  | 12.0 | % |  |  | x
2.2 Anaerobic digestion (system boundary > Biomass Conversion I in Figure 10.)
Gas power |  | 1.241 | kW | x
Power digester heating |  | 105.0 | kW | x |  | (x) | A lump sum of 35 % of the heat extraction
Losses (thermal + chemical) |  | — | kW |  |  | (x) | Not measurable
Chemical efficiency |  | 72.2 | % | x
2.3 Gas utilisation of CHP plant (system boundary > Biomass Conversion II in Figure 10.)
Electrical efficiency of prime mover (gross) |  | 39.0 | % |  |  | x
Thermal efficiency of prime mover (gross) |  | 45.0 | % |  |  | x
Total efficiency of prime mover (gross) |  | 84.0 | % | x
Nominal heat output |  | 577.0 | kW |  |  | x
Electrical nominal power |  | 500.0 | kW |  |  | x
2.4 Total plant (system boundary > Biomass Conversion II in Figure 10.)
Electrical plant efficiency (net) |  | 24.5 | % | x
Thermal plant efficiency (net) |  | 10.7 | % | x |  |  | Heat output minus on-site consumption
Total system / plant efficiency (net) |  | 35.2 | % | x
3 Plausibility check |  | Data | Unit | Calculation | Measurement | Assumption | Explanation of data origin: measuring method, calculation path, source of the assumption
3.1 Energy balance (system boundary: ...)
Input | Substrate power | 1.718 | kW | x
| Power of auxiliary energy (energy delivered) | 0 | kW | x
| Energy input | 1.718 | kW | x
Output | Electrical plant power | 457.0 | kW | x |  |  | At 8,000 h/a full load; corresponds to the rated power
| Thermal plant power | 527.0 | kW | x |  |  | At 8,000 h/a full load
| Power by-products | 0 | kW | x |  |  | None
| Losses (thermal + chemical) | 0 | kW | x |  |  | None; unused energy potential from digestate + losses
| Energy output | 984.0 | kW | x |  |  | In the example, only sum of electrical and thermal power of plant / system
3.2 Material balance (system boundary: ...)
Input | Mass flow of substrate | 42.0 | t/d | x | (x) |  | Sum of the substrates
| Mass flow of auxiliaries | 0 | t/d | x |  |  | Sum of auxiliaries, e.g. for desulphurisation, trace elements, etc.
| Input mass flow | 42.0 | t/d | x
Output | Mass flow of biogas | 6.5 | t/d | x |  |  | Calculation at a density of 1.25 kg/m3
| Mass flow of by-products | — | t/d | x |  |  | No by-products
| Mass flow of residues | 32.7 | t/d | x |  |  | Volume of fermenter residue incl. condensate
| Output mass flow | 35.2 | t/d | x